{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":11,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ADEA-A"]
[]
[]
[]
[]
["","","","","","ADEA35A2VEB","ADEA50A2VEB","ADEA60A2VEB","ADEA71A2VEB","ADEA100A2VEB","ADEA125A2VEB"]
["Sound pressure level","Heating","","High","dBA","37","37","31","31","36","38"]
["","","","Medium","dBA","34","34","28","28","33","35"]
["","","","Low","dBA","29","29","25","25","30","32"]
["","Cooling","","Medium","dBA","32","32","28","28","32","35"]
["","","","Low","dBA","29","29","25","25","30","32"]
["","","","High","dBA","35","35","30","30","34","37"]
["Standard Accessories","Operation manual","","","","1","1","1","1","1","1"]
["","Installation manual","","","","1","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1","1"]
["","Metal clamp for drain hose","","","","1","1","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8","8","8"]
["","Screws","","","","40","40","40","40","40","40"]
["","Insulation for fitting","","","","2","2","2","2","2","2"]
["","Sealing pads","","","","5","5","5","5","5","5"]
["","Clamps","","","","4","4","4","4","4","4"]
["Control systems","Wired remote control","","","","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52"]
["","Infrared remote control","","","","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66"]
["Cooling capacity","Total capacity","","Nom.","kW","","","","","","14.00"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","6.35","9.52","9.52","9.52"]
["","Gas","","OD","mm","9.52","12.70","12.70","15.90","15.90","15.90"]
["","Drain","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Sound power level","Cooling","","","dBA","60","60","56","56","58","62"]
["Dimensions","Unit","","Width","mm","700","700","1,000","1,000","1,400","1,400"]
["","","","Depth","mm","800","800","800","800","800","800"]
["","","","Height","mm","245","245","245","245","245","245"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["","Colour","","","","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)"]
["Weight","Unit","","","kg","28.0","28.0","35.0","35.0","46.0","46.0"]
["Fan","External static pressure","","High","Pa","150","150","150","150","150","150"]
["","","","Nom.","Pa","30","30","30","30","40","50"]
["","Air flow rate","Heating","High","m³/min","15.0","15.0","18.0","18.0","29.0","34.0"]
["","","","Medium","m³/min","12.5","12.5","15.0","15.0","26.0","29.0"]
["","","","Low","m³/min","10.5","10.5","12.5","12.5","23.0","23.5"]
["","","Cooling","Low","m³/min","10.5","10.5","12.5","12.5","23.0","23.5"]
["","","","Medium","m³/min","12.5","12.5","15.0","15.0","26.0","29.0"]
["","","","High","m³/min","15.0","15.0","18.0","18.0","29.0","34.0"]
["Drain-up height","mm","","","","625","625","625","625","625","625"]
["Heating capacity","Total capacity","","Nom.","kW","","","","","","13.50"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Sound power level is an absolute value that a sound source generates.","(1) - Sound power level is an absolute value that a sound source generates.","(1) - Sound power level is an absolute value that a sound source generates.","(1) - Sound power level is an absolute value that a sound source generates.","(1) - Sound power level is an absolute value that a sound source generates.","(1) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data","(2) - See separate drawing for electrical data"]