{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":8,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYQ-ACV3"]
[]
[]
[]
[]
["","","","","","EWYQ009ACV3","EWYQ010ACV3","EWYQ011ACV3"]
["Cooling capacity","Nom.","","","kW","12.2 (1), 8.60 (2)","13.6 (1), 9.60 (2)","11.1 (2), 15.7 (1)"]
["Capacity control","Method","","","","Inverter controlled","Inverter controlled","Inverter controlled"]
["Power input","Cooling","","Nom.","kW","2.83 (2), 2.85 (1)","3.28 (2), 3.41 (1)","3.90 (2), 4.13 (1)"]
["EER","","","","","3.05 (2), 4.27 (1)","2.93 (2), 4.00 (1)","2.85 (2), 3.79 (1)"]
["Dimensions","Unit","","Depth","mm","382","382","382"]
["","","","Height","mm","1,435","1,435","1,435"]
["","","","Width","mm","1,420","1,420","1,420"]
["Weight","Unit","","","kg","180","180","180"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Painted galvanized steel plate","Painted galvanized steel plate","Painted galvanized steel plate"]
["Air heat exchanger","Type","","","","Hi-XSS (8)","Hi-XSS (8)","Hi-XSS (8)"]
["Fan","Quantity","","","","2","2","2"]
["","Type","","","","Propeller fan","Propeller fan","Propeller fan"]
["Fan motor","Drive","","","","Direct drive","Direct drive","Direct drive"]
["Compressor","Quantity","","","","1","1","1"]
["","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven"]
["Operation range","Air side","Cooling","Min.","°CDB","10","10","10"]
["","","","Max.","°CDB","46","46","46"]
["","Water side","Evaporator","Min.","°CDB","5","5","5"]
["","","","Max.","°CDB","20","20","20"]
["Sound power level","Cooling","","Nom.","dBA","64.0 (3)","64.0 (3)","64.0 (3)"]
["Sound pressure level","Cooling","","Nom.","dBA","50 (3)","50 (3)","50 (3)"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Circuits","","Quantity","","1","1","1"]
["Power supply","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","230","230","230"]
["","Voltage range","","Min.","%","-10","-10","-10"]
["","","","Max.","%","10","10","10"]
["Notes","","","","","(1) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)","(1) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)","(1) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)"]
["","","","","","(2) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )","(2) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )","(2) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )"]
["","","","","","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Including piping + PHE; excluding expansion vessel","(5) - Including piping + PHE; excluding expansion vessel","(5) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(6) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(6) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(6) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]
["","","","","","(7) - Contains fluorinated greenhouse gases","(7) - Contains fluorinated greenhouse gases","(7) - Contains fluorinated greenhouse gases"]