{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":67,"n_cols":13,"rows_kept":67,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXCQ-A"]
[]
[]
[]
[]
["","","","","","FXCQ20AVEB","FXCQ25AVEB","FXCQ32AVEB","FXCQ40AVEB","FXCQ50AVEB","FXCQ63AVEB","FXCQ80AVEB","FXCQ125AVEB"]
["Sound pressure level","Heating","","At high fan speed","dBA","32.0","34.0","34.0","36.0","37.0","39.0","42.0","46.0"]
["","","","At low fan speed","dBA","28.0","29.0","30.0","31.0","31.0","32.0","33.0","38.0"]
["","","","At medium fan speed","dBA","30.0","31.0","32.0","33.0","35.0","37.0","38.0","42.0"]
["","Cooling","","At low fan speed","dBA","28.0","29.0","30.0","31.0","31.0","32.0","33.0","38.0"]
["","","","At high fan speed","dBA","32.0","34.0","34.0","36.0","37.0","39.0","42.0","46.0"]
["","","","At medium fan speed","dBA","30.0","31.0","32.0","33.0","35.0","37.0","38.0","42.0"]
["Standard Accessories","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Declaration of conformity","","","","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity"]
["","Installation pattern","","","","Installation pattern","Installation pattern","Installation pattern","Installation pattern","Installation pattern","Installation pattern","Installation pattern","Installation pattern"]
["","Washer for hanger bracket","","","","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket"]
["","Clamp metal","","","","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal"]
["","Drain hose","","","","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose"]
["","Joint insulating material","","","","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material"]
["","Washer clamp","","","","Washer clamp","Washer clamp","Washer clamp","Washer clamp","Washer clamp","Washer clamp","Washer clamp","Washer clamp"]
["","Sealing material","","","","Sealing material","Sealing material","Sealing material","Sealing material","Sealing material","Sealing material","Sealing material","Sealing material"]
["","Clamps","","","","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps"]
["","Screws","","","","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws"]
["","Insulation piping cover for drain piping","","","","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping","Insulation piping cover for drain piping"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.031","0.039","0.039","0.041","0.059","0.063","0.090","0.149"]
["","Heating","","At high fan speed","kW","0.028","0.035","0.035","0.037","0.056","0.060","0.086","0.146"]
["Cooling capacity","Total capacity","","At high fan speed","kW","2.2 (1)","2.8 (1)","3.6 (1)","4.5 (1)","5.6 (1)","7.1 (1)","9.0 (1)","14.0 (1)"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","6.35","6.35","6.35","9.52","9.52","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","15.9","15.9","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Sound power level","Cooling","","At high fan speed","dBA","48","50","50","52","53","55","58","62"]
["Air filter","Type","","","","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance"]
["Dimensions","Unit","","Width","mm","775","775","775","775","990","990","1,445","1,445"]
["","","","Depth","mm","620","620","620","620","620","620","620","620"]
["","","","Height","mm","305","305","305","305","305","305","305","305"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","19","19","19","19","22","25","33","38"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","10.5","11.5","11.5","12","15","16","26","32"]
["","","","At low fan speed","m³/min","7.5","8","8","8.5","10.5","11.5","18.5","22.5"]
["Decoration panel","Weight","","","kg","10","10","10","10","11","11","13","13"]
["","Model","","","","BYBCQ40HW1","BYBCQ40HW1","BYBCQ40HW1","BYBCQ40HW1","BYBCQ63HW1","BYBCQ63HW1","BYBCQ125HW1","BYBCQ125HW1"]
["","Dimensions","","Height","mm","55","55","55","55","55","55","55","55"]
["","","","Depth","mm","700","700","700","700","700","700","700","700"]
["","","","Width","mm","1,070","1,070","1,070","1,070","1,285","1,285","1,740","1,740"]
["","Colour","","","","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)","Fresh white (6.5Y 9.5/0.5)"]
["Heating capacity","Total capacity","","At high fan speed","kW","2.5 (2)","3.2 (2)","4.0 (2)","5.0 (2)","6.3 (2)","8.0 (2)","10.0 (2)","16.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16","16"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA"]
["","","","","","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A","(8) - Next lower standard fuse rating minimum 16A"]
["","","","","","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker"]
["","","","","","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases"]