{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":92,"n_cols":8,"rows_kept":92,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSCQ-TV1"]
[]
[]
[]
[]
["","","","","","RXYSCQ4TMV1B","RXYSCQ5TMV1B","RXYSCQ6TMV1B"]
["Sound pressure level","Cooling","","Nom.","dBA","51.0 (8)","52.0 (8)","53.0 (8)"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Operation manual","","","","1","1","1"]
["","Connection pipes","","","","1","1","1"]
["Capacity range","HP","","","","4","5","6"]
["Operation range","Cooling","","Max.","°CDB","46.0","46.0","46.0"]
["","","","Min.","°CDB","-5.0","-5.0","-5.0"]
["","Heating","","Min.","°CWB","-20.0","-20.0","-20.0"]
["","","","Max.","°CWB","15.5","15.5","15.5"]
["ηs,c","%","","","","322.8","303.4","281.3"]
["Maximum number of connectable indoor units","","","","","64 (6)","64 (6)","64 (6)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","8.9","10.3","11.4"]
["","","","EERd","","5.5","5.0","4.5"]
["","D Condition (20°C - 27/19)","","Pdc","kW","4.8","4.9","5.0"]
["","","","EERd","","18.6","19.9","21.2"]
["","A Condition (35°C - 27/19)","","EERd","","3.2","2.7","2.7"]
["","","","Pdc","kW","12.1","14.0","15.5"]
["","C Condition (25°C - 27/19)","","EERd","","11.4","10.5","8.9"]
["","","","Pdc","kW","5.7","6.6","7.3"]
["SCOP","","","","","4.6","4.7","4.7"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","89","89","89"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","3.7","3.7","3.7"]
["","Type","","","","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Heating","Nom.","6°CWB","kW","2.82 (5)","3.44 (5)","4.18 (5)"]
["Indoor index connection","Min.","","","","50.0","62.5","70.0"]
["","Max.","","","","130.0","162.5","182.0"]
["Cooling capacity","Prated,c","","","kW","12.1 (1)","14.0 (1)","15.5 (1)"]
["COP at nom. capacity","6°CWB","","","kW/kW","4.29","4.07","3.71"]
["Recommended combination","","","","","3 x FXSQ25A2VEB + 1 x FXSQ32A2VEB","4 x FXSQ32A2VEB","2 x FXSQ32A2VEB + 2 x FXSQ40A2VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","2.8","2.7","2.7"]
["","","","Pdh (declared heating cap)","kW","8.4","9.7","10.7"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","4.0","4.0","4.0"]
["","","","COPd (declared COP)","","7.9","8.1","8.2"]
["","B Condition (2°C)","","COPd (declared COP)","","4.5","4.5","4.4"]
["","","","Pdh (declared heating cap)","kW","4.5","5.2","5.8"]
["","C Condition (7°C)","","COPd (declared COP)","","6.3","6.4","6.6"]
["","","","Pdh (declared heating cap)","kW","3.4","3.4","3.7"]
["","A Condition (-7°C)","","COPd (declared COP)","","3.2","3.1","3.1"]
["","","","Pdh (declared heating cap)","kW","7.4","8.5","9.5"]
["","TBivalent","","Pdh (declared heating cap)","kW","8.4","9.7","10.7"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10"]
["","","","COPd (declared COP)","","2.8","2.7","2.7"]
["Piping connections","Liquid","","OD","mm","10","10","10"]
["","","","Type","","Flare connection","Flare connection","Flare connection"]
["","Total piping length","System","Actual","m","300 (9)","300 (9)","300 (9)"]
["","Gas","","OD","mm","15.9","15.9","19.1"]
["","","","Type","","Flare connection","Flare connection","Flare connection"]
["SEER","","","","","8.1","7.7","7.1"]
["Sound power level","Cooling","","Nom.","dBA","68.0 (7)","69.0 (7)","70.0 (7)"]
["Dimensions","Unit","","Width","mm","940","940","940"]
["","","","Depth","mm","460","460","460"]
["","","","Height","mm","823","823","823"]
["ηs,h","%","","","","182.3","185.1","186.0"]
["Heating capacity","Prated,h","","","kW","12.1 (5)","14.0 (5)","15.5 (5)"]
["","Nom.","","6°CWB","kW","12.1 (5)","14.0 (5)","15.5 (5)"]
["Power supply","Phase","","","","1~","1~","1~"]
["","Name","","","","V1","V1","V1"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included"]
["","","","","","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included"]
["","","","","","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included"]
["","","","","","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%)."]
["","","","","","(7) - Sound power level is an absolute value that a sound source generates.","(7) - Sound power level is an absolute value that a sound source generates.","(7) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(9) - Refer to refrigerant pipe selection or installation manual","(9) - Refer to refrigerant pipe selection or installation manual","(9) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(15) - TOCA means the total value of each OC set.","(15) - TOCA means the total value of each OC set.","(15) - TOCA means the total value of each OC set."]
["","","","","","(16) - FLA means the nominal running current of the fan","(16) - FLA means the nominal running current of the fan","(16) - FLA means the nominal running current of the fan"]
["","","","","","(17) - Maximum allowable voltage range variation between phases is 2%.","(17) - Maximum allowable voltage range variation between phases is 2%.","(17) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control)."]
["","","","","","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality."]
["","","","","","(21) - Sound values are measured in a semi-anechoic room.","(21) - Sound values are measured in a semi-anechoic room.","(21) - Sound values are measured in a semi-anechoic room."]
["","","","","","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(23) - Ssc: Short-circuit power","(23) - Ssc: Short-circuit power","(23) - Ssc: Short-circuit power"]
["","","","","","(24) - For detailed contents of standard accessories, see installation/operation manual","(24) - For detailed contents of standard accessories, see installation/operation manual","(24) - For detailed contents of standard accessories, see installation/operation manual"]