{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MY1"]
[]
[]
[]
[]
["","","","","","AZAS100M7Y1B","AZAS125M7Y1B","AZAS140M7Y1B"]
["Dimensiones","Unidad","","Altura","mm","990","990","990"]
["","","","Anchura","mm","940","940","940"]
["","","","Profundidad","mm","320","320","320"]
["Peso","Unidad","","","kg","","70"]
["Compresor","Type","","","","","Compresor swing herméticamente sellado"]
["Límites de funcionamiento","Refrigeración","Ambiente","Mín.","°CBS","-5","-5","-5"]
["","","","Máx.","°CBS","46","46","46"]
["","Calefacción","Ambiente","Mín.","°CBH","-15","-15","-15"]
["","","","Máx.","°CBH","15.5","15.5","15.5"]
["Nivel de potencia sonora","Refrigeración","","","dBA","70","71","73"]
["","Calefacción","","","dBA","","71","73 (1)"]
["Nivel de presión sonora","Refrigeración","","Nom.","dBA","53","53","54"]
["","Calefacción","","Nom.","dBA","57","57","57"]
["Refrigerante","Tipo","","","","R-32","R-32","R-32"]
["","Carga","","","kg","2.60","2.60","2.90"]
["Refrigerante","GWP","","","","","675"]
["Refrigerante","Carga","","","tCO2Eq","1.76","1.76","1.96"]
["Conexiones de tubería","Líquido","","D.E.","mm","9.52","9.52","9.52"]
["Piping connections","Gas","","D.E.","mm","","15.9"]
["Conexiones de tubería","Longitud de tubería","Máx.","Ud. ext. – Ud. int.","m","30","30","30"]
["","","Sistema","Equivalente","m","50","50","50"]
["","","","Sin carga","m","30","30","30"]
["","Carga de refrigerante adicional.","","","kg/m","Consulte el manual de instalación","Consulte el manual de instalación","Consulte el manual de instalación"]
["","Diferencia de nivel","Ud. int. – Ud. ext.","Máx.","m","30.0","30.0","30.0"]
["","","Ud. int. – Ud. int.","Máx.","m","0.5","0.5","0.5"]
["Accesorios estándar","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Alimentación eléctrica","Fase","","","","3~","3~","3~"]
["","Alimentación eléctrica-=-Frecuencia","","Frecuencia","","50","50","50"]
["","Alimentación eléctrica-=-Tensión","","Tensión","","380-415","380-415","380-415"]
["Corriente (50 Hz)","Corriente (50 Hz)-=-Amperios máximos del fusible (MFA)","","Corriente (50 Hz)-=-Amperios máximos del fusible (MFA)-=-A","","","16"]
["Notas","","","","","","(1) - Según ENER Lot 21","(1) - Según ENER Lot 21"]
["Peso","Unidad","","","kg","70","","77"]
["Compresor","Tipo","","","","Compresor swing herméticamente sellado","","Compresor swing herméticamente sellado"]
["Refrigerante","GWP","","","","675","","675"]
["Conexiones de tubería","Gas","","D.E.","mm","15.9","","15.9"]
["Corriente - 50Hz","Amperios máximos del fusible (MFA)","","","A","16","","16"]