{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":6,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EBLA-D3W17"]
[]
[]
[]
[]
["","","","","","EBLA16DA3W17"]
["Capacidad de calefacción","Nom.","","","kW","16.0 (1) (2)"]
["Capacidad de refrigeración","Nom.","","","kW","14.0 (3), 15.3 (4)"]
["Capacidad del calentador","Etapa 1","","","kW","3"]
["Consumo","Refrigeración","","Nom.","kW","4.58 (3), 3.24 (4)"]
["","Calefacción","","Nom.","kW","3.53 (1), 4.56 (2)"]
["COP","","","","","4.53 (1), 3.51 (2)"]
["EER","","","","","3.06 (3), 4.74 (4)"]
["Dimensiones","Unidad","","Altura","mm","870"]
["","","","Anchura","mm","1380"]
["","","","Profundidad","mm","460"]
["Peso","Unidad","","","kg","149"]
["Ventilador","Caudal de aire","Calefacción","Alto","m³/min","85.0"]
["","","Refrigeración","Alto","m³/min","85.0"]
["Límites de funcionamiento","Calefacción","Lado del agua","Mín.","°C","15 (6)"]
["","","","Máx.","°C","60 (6)"]
["","Refrigeración","Ambiente","Mín.","°CBS","10"]
["","","","Máx.","°CBS","43"]
["","","Lado del agua","Mín.","°C","5"]
["","","","Máx.","°C","22"]
["","Agua caliente sanitaria","Ambiente","Mín.","°CBS","-25"]
["","","","Máx.","°CBS","35"]
["","","Lado del agua","Mín.","°C","25"]
["","","","Máx.","°C","55 (6)"]
["Refrigerante","Tipo","","","","R-32"]
["","GWP","","","","675"]
["","Carga","","","kg","3.80"]
["","Carga","","","tCO2Eq","2.57"]
["Calefacción de habitaciones","Temperatura del agua de salida en clima medio 55°C","General","SCOP","","3.37"]
["Calef. de habitaciones","Temp. del agua de salida, clima medio 55°C","General","Clase de efic. estac. de calef. de habitaciones","","A++"]
["Calefacción de habitaciones","Temperatura del agua de salida en clima medio 35°C","General","SCOP","","4.69"]
["Calef. de habitaciones","Temp. del agua de salida, clima medio 35°C","General","Clase de efic. estac. de calef. de habitaciones","","A+++"]
["Componente compresor","Alimentación eléctrica principal","","Fase","","3N~"]
["","","","Tensión","V","400"]
["Alimentación eléctrica","Nombre","","","","W1"]
["","Fase","","","","3~"]
["","Frecuencia","","","Hz","50"]
["","Tensión","","","V","400"]
["Notas","","","","","(1) - Condición: Ta BS/BH 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(2) - Condición: Ta BS/BH 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(3) - Refrigeración: EW 12°C; LW 7°C; condiciones ambientales: 35 °CBS"]
["","","","","","(4) - Refrigeración: EW 23°C; LW 18°C; condiciones ambientales: 35 °CBS"]
["","","","","","(5) - Conforme a EN14825"]
["","","","","","(6) - Encontrará más detalles en el diagrama de límites de funcionamiento."]
["","","","","","(7) - En función del modo de funcionamiento; consulte el manual de instalación."]