{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":27,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWFH-TZPSD"]
[]
[]
[]
[]
["","","","","","","EWFH225TZPSD1","EWFH265TZPSD1","EWFH295TZPSD1","EWFH340TZPSD1","EWFH395TZPSD1","EWFH420TZPSD1","EWFH490TZPSD1","EWFH500TZPSD2","EWFH540TZPSD2","EWFH545TZPSD1","EWFH615TZPSD2","EWFH645TZPSD2","EWFH700TZPSD2","EWFH770TZPSD2","EWFH845TZPSD2","EWFH900TZPSD2","EWFH960TZPSD2","EWFHC10TZPSD2","EWFHH10TZPSD2","EWFHH11TZPSD2","EWFHC12TZPSD2"]
["Capacidad de refrigeración","Nom.","","","","kW","308.33","364.24","398.93","460.16","543.56","573.55","653.01","684.17","730.46","717.11","834.66","875.71","945.17","1037.99","1153.08","1224.16","1446.82","1352.07","1439.29","1532.91","1610.74"]
["Control de capacidad","Método","","","","","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua","Regulación continua"]
["Control de capacidad","Capacidad mínima","","","","%","21.5","19","16.5","27.5","23","21.5","19","10","10","30","15","13.5","12.5","11.5","10.5","10","10","10","10","13.5","13.5"]
["Consumo","Refrigeración","","","Nom.","kW","73.38","83.69","98.43","100.78","129.36","132.95","160.4","158.93","165.04","163.72","195.61","206.58","231.09","250.36","271.38","309.91","394.23","352.29","378.66","367.25","385.07"]
["EER","","","","","","4.2","4.35","4.05","4.57","4.2","4.31","4.07","4.3","4.43","4.38","4.27","4.24","4.09","4.15","4.25","3.95","3.67","3.84","3.8","4.17","4.18"]
["IPLV","","","","","","6.738","6.736","6.579","7.506","7.214","7.271","7.135","6.819","6.956","6.73","7.347","7.226","7.016","7.052","7.143","6.966","6.615","6.787","6.825","6.965","7.041"]
["SEER","","","","","","6.008","6.095","6.081","6.58","6.397","6.579","6.481","6.199","6.24","5.753","6.646","6.55","5.945","6.46","6.506","6.388","5.929","6.3","5.568","6.031","6.095"]
["Dimensiones","Unidad","","","Profundidad","mm","3640","4720","4720","5800","5800","6880","6880","6880","7960","6880","7960","7960","7960","9040","10120","10120","11200","11200","12280","12280","13360"]
["","","","","Altura","mm","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553"]
["","","","","Anchura","mm","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238"]
["Peso","Peso operativo","","","","kg","3628","4254","4259","5223.1","5233.1","5813.1","5939.3","6391","6971","6618.3","7900","7905","7910","8765","9329","9339","11225","11235","11797","12476","13061"]
["Peso","Unidad","","","","kg","3307","3846","3846","4720","4720","5229","5315","5336","5846","5984","6358","6358","6358","6957","7519","7519","8341","8341","8892","9561","10070"]
["Carcasa","Color","","","","","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil","Blanco marfil"]
["Carcasa","Material","","","","","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada","Lámina de acero galvanizado pintada"]
["Evaporador del intercambiador de calor de agua","Tipo","","","","","Placa cobresoldada","Placa cobresoldada","Placa cobresoldada","Placa cobresoldada","Placa cobresoldada","Placa cobresoldada","Placa cobresoldada","Cuerpo y tubo","Cuerpo y tubo","Placa cobresoldada","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo","Cuerpo y tubo"]
["","Volumen de agua","","","","l","40","48","48","58.1","58.1","58.1","76.3","289","289","76.3","492","492","492","583","546","546","1043","1043","1011","1011","1011"]
["Intercambiador de calor de agua: evaporador","Caída de presión del agua","","Refrigeración","Nom.","kPa","11.16","12.17","14.48","17.51","23.47","26.02","20.14","23.25","25.85","23.77","35.01","37.4","42.13","39.81","60.34","66.12","43","38.9","29.48","32.39","34.95"]
["Intercambiador de calor de aire","Tipo","","","","","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal"]
["Ventilador","Cantidad","","","","","6","8","8","10","10","12","12","12","14","12","14","14","14","16","18","18","20","20","22","22","24"]
["","Tipo","","","","","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo","Helicoidal directo"]
["","Caudal de aire","","Refrigeración","Nom.","l/s","33765","45020","45020","56275","56275","67530","67530","67530","78785","67530","78785","78785","78785","90040","101295","101295","112550","112550","123805","123805","135060"]
["Motor del ventilador","Transmisión","","","","","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas","Sin escobillas"]
["Compresor","Compresor-=-Cantidad_","","","","","1","1","1","1","1","1","1","2","2","1","2","2","2","2","2","2","2","2","2","2","2"]
["Compresor","Tipo","","","","","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo","Compresor de tornillo"]
["Límites de funcionamiento","Lado del aire","","Refrigeración","Mín.","°CBS","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","","Máx.","°CBS","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46"]
["","Lado del agua","","Límites de funcionamiento-=-Lado del agua-=-Refrigeración","Límites de funcionamiento-=-Lado del agua-=-Refrigeración-=-Mín.-=-°CBS","°CBS","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4"]
["","","","","Límites de funcionamiento-=-Lado del agua-=-Refrigeración-=-Máx.-=-°CBS","°CBS","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18"]
["Nivel de potencia sonora","Refrigeración","","","Nom.","dBA","97.5","98.1","102.6","95.7","98.7","100.1","104.6","100.6","100.9","99","96.6","97.5","99.3","101","102.3","104.2","106.5","106.9","105.5","102.4","102.8"]
["Nivel de presión sonora","Refrigeración","","","Nom.","dBA","77.7","77.8","82.3","75","77.9","78.9","83.4","79.4","79.4","77.8","75.1","76","77.8","79","80.1","81.9","84","84.3","82.7","79.5","79.7"]
["Refrigerante","Tipo","","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["Refrigerante","GWP","","","","","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7"]
["Refrigerante","Carga","","","","kg","30","35","40","45","55","60","65","70","75","75","85","90","95","105","115","125","130","140","150","160","170"]
["","Circuitos","","","Cantidad","","1","1","1","1","1","1","1","2","2","1","2","2","2","2","2","2","2","2","2","2","2"]
["Conexiones de tubería","Entrada/salida de agua del evaporador (D.E.)","","","","","88.9","88.9","88.9","139.7","139.7","139.7","139.7","168.3","168.3","139.7","219.1","219.1","219.1","219.1","219.1","219.1","273","273","273","273","273"]
["Alimentación eléctrica","Fase","","","","","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3"]
["","Alimentación eléctrica-=-Frecuencia","","","Frecuencia","","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Alimentación eléctrica-=-Tensión","","","Tensión","","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["","Límites de tensión","","Mín.","Mín.","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Máx.","Máx.","","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10"]
["Unidad","Corriente de arranque","","Unidad-=-Corriente de arranque-=-Máx.","Máx.","","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["","Corriente de func.","Refrigeración","Unidad-=-Corriente de func.-=-Refrigeración-=-Nom.","Nom.","","121","136","161","170","213","219","259","259","268","269","332","348","385","414","445","503","696","639","605","596","623"]
["","","","Unidad-=-Corriente de func.-=-Máx.","Máx.","","183","214","235","258","301","330","367","375","406","425","432","458","505","558","609","647","694","731","779","875","923"]
["","Unidad-=-Corriente de la unidad máx. para el tamaño de los cables","","","Corriente de la unidad máx. para el tamaño de los cables","","201","235","258","283","331","363","404","412","444","467","476","503","556","614","670","712","764","804","857","962","1015"]