{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":85,"n_cols":9,"rows_kept":85,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FDXM-F9"]
[]
[]
[]
[]
["","","","","","FDXM25F3V1B9","FDXM35F3V1B9","FDXM50F3V1B9","FDXM60F3V1B9"]
["Nivel de presión sonora","Calefacción","","Alto","dBA","35.0","35.0","","38.0"]
["","","","Medio","dBA","33.0","33.0","","35.0"]
["","","","Bajo","dBA","27.0","27.0","","30.0"]
["","Refrigeración","","Medio","dBA","33.0","33.0","","35.0"]
["","","","Bajo","dBA","27.0","27.0","","30.0"]
["","","","Alto","dBA","35.0","35.0","","38.0"]
["Accesorios estándar","Manual de instalación","","","","1","1","","1"]
["","Manual de uso","","","","1","1","","1"]
["","Aislamiento para adaptador","","","","1","1","","1"]
["","Almohadilla de sellado","","","","1","1","","1"]
["","Abrazadera metálica","","","","1","1","","1"]
["","Tubo flexible de drenaje","","","","1","1","","1"]
["","Arandela para ménsula de suspensión","","","","8","8","","8"]
["","Material de sellado","","","","2","2","","2"]
["","Abrazaderas","","","","6","6","","6"]
["","Arandela para placa de fijación","","","","4","4","","4"]
["","Tornillos para bridas de conducto","","","","1","1","","1"]
["","Filtro de aire","","","","1","1","","1"]
["Conexiones de tubería","Líquido","","D.E.","mm","6.35","6.35","","6.35"]
["","Gas","","D.E.","mm","9.50","9.50","","12.70"]
["","Drenaje","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","","VP20 (I.D. 20/O.D. 26)"]
["Consumo","Refrigeración","","Nom.","kW","0.036","0.036","","0.060"]
["","Calefacción","","Nom.","kW","0.036","0.036","","0.060"]
["Sound power level","Refrigeración","","","dBA","53.0","53.0","","56.0"]
["","Calefacción","","","dBA","53.0","53.0","","56.0"]
["Dimensiones","Unidad","","Anchura","mm","750","750","","1,150"]
["","","","Profundidad","mm","620","620","","620"]
["","","","Altura","mm","200","200","","200"]
["Peso","Unidad","","","kg","21","21","","28"]
["Ventilador","Presión estática externa","","Nom.","Pa","30","30","","40"]
["","Caudal de aire","Calefacción","Alto","m³/min","8.7","8.7","","16.0"]
["","","","Medio","m³/min","8.0","8.0","","14.8"]
["","","","Bajo","m³/min","7.3","7.3","","13.5"]
["","","Refrigeración","Bajo","m³/min","7.3","7.3","","13.5"]
["","","","Medio","m³/min","8.0","8.0","","14.8"]
["","","","Alto","m³/min","8.7","8.7","","16.0"]
["Power supply","Fase","","","","1~","1~","","1~"]
["","Frecuencia","","","Hz","50","50","","50"]
["","Tensión","","","V","220-240","220-240","","220-240"]
["Notas","","","","","(1) - Consulte en el plano independiente con los datos eléctricos.","(1) - Consulte en el plano independiente con los datos eléctricos.","","(1) - Consulte en el plano independiente con los datos eléctricos."]
["Consumo","Refrigeración","","Nom.","kW","","","0.060"]
["","Calefacción","","Nom.","kW","","","0.060"]
["Dimensiones","Unidad","","Altura","mm","","","200"]
["","","","Anchura","mm","","","1150"]
["","","","Profundidad","mm","","","620"]
["Peso","Unidad","","","kg","","","28"]
["Ventilador","Caudal de aire","Refrigeración","Alto","m³/min","","","15.8"]
["","","","Medio","m³/min","","","14.6"]
["","","","Bajo","m³/min","","","13.3"]
["","","Calefacción","Alto","m³/min","","","15.8"]
["","","","Medio","m³/min","","","14.6"]
["","","","Bajo","m³/min","","","13.3"]
["","Presión estática externa","","Nom.","Pa","","","40"]
["Nivel de potencia sonora","Refrigeración","","","dBA","","","55.0"]
["","Calefacción","","","dBA","","","55.0"]
["Nivel de presión sonora","Refrigeración","","Alto","dBA","","","38.0"]
["","","","Medio","dBA","","","35.0"]
["","","","Bajo","dBA","","","30.0"]
["","Calefacción","","Alto","dBA","","","38.0"]
["","","","Medio","dBA","","","35.0"]
["","","","Bajo","dBA","","","30.0"]
["Conexiones de tubería","Líquido","","D.E.","mm","","","6.35"]
["","Gas","","D.E.","mm","","","12.70"]
["","Drenaje","","","","","","VP20 (I.D. 20/O.D. 26)"]
["Accesorios estándar","Installation manual","","","","","","1"]
["","Washer for hanger bracket","","","","","","8"]
["","Operation manual","","","","","","1"]
["","Clamp metal","","","","","","1"]
["","Clamps","","","","","","6"]
["","Drain hose","","","","","","1"]
["","Filtro de aire","","","","","","1"]
["","Insulation for fitting","","","","","","1"]
["","Screws for duct flanges","","","","","","1"]
["","Sealing material","","","","","","2"]
["","Sealing pad","","","","","","1"]
["","Washer fixing plate","","","","","","4"]
["Alimentación eléctrica","Fase","","","","","","1~"]
["","Frecuencia","","","Hz","","","50"]
["","Tensión","","","V","","","220-240"]