{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3--"]
["Capacidad de refrigeración (condiciones estándar)","Capacidad sensible, 4 tubos","","Bajo","kW","3.26"]
["","","","Alto","kW","5.58"]
["","Capacidad total, 4 tubos","","Bajo","kW","4.35"]
["","","","Alto","kW","7.15"]
["Capacidad de calefacción (condiciones estándar)","Capacidad, 4 tubos","","Bajo","kW","5.34"]
["","","","Alto","kW","8.82"]
["Consumo","Bajo","","","kW","0.02"]
["","Alto","","","kW","0.069"]
["Dimensiones","Unidad","","Altura","mm","287"]
["","","","Anchura","mm","837"]
["","","","Profundidad","mm","921"]
["Peso","Unidad","","","kg","27"]
["Ventilador","Caudal de aire","","Bajo","m³/h","686"]
["","","","Alto","m³/h","1,296"]
["Nivel total de potencia sonora","Bajo","","","dBA","36"]
["","Alto","","","dBA","52"]
["Nivel de presión sonora","Bajo","","","dBA","23"]
["","Alto","","","dBA","39"]
["Flujo de agua","Refrigeración","","Bajo","l/h","776"]
["","","","Alto","l/h","1,295"]
["","Calefacción","","Bajo","l/h","459"]
["","","","Alto","l/h","759"]
["","Caída de presión del agua","Refrigeración","Bajo","kPa","13"]
["","","","Alto","kPa","25"]
["","","Calefacción","Bajo","kPa","13"]
["","","","Alto","kPa","24"]
["Conexiones de tubería","Agua","","Entrada","","3/4\" BSP (rosca hembra)"]
["","","","Salida","","3/4\" BSP (rosca hembra)"]
["","Drenaje","","D.E.","mm","VP25 (Diá. ext. 32; diá. int. 25)"]
["Alimentación eléctrica","Tipo","","","","230 / 1 / 50"]
["","Fase","","","","1~"]
["","Frecuencia","","","Hz","50"]
["","Tensión","","","V","230"]
["Notas","","","","","(1) - Refrigeración: aire 27°CBS, 19°CBH; agua de entrada 7℃; agua de salida 12℃"]
["","","","","","(2) - Calefacción: 2 tubos: aire 20°CBS, 15°CBH; agua de entrada 45°C; agua de salida 40°C;"]
["","","","","","(3) - Calefacción: 4 tubos: aire 20°CBS, 15°CBH; agua de entrada 65°C; agua de salida 55°C;"]
["","","","","","(4) - No deje que entre agua con una temperatura inferior a 5 °C o superior a 90 °C en la unidad, dado que podría dañarla"]
["","","","","","(5) - Flujo de aire: 20 °C BS, 15 °C BH; 230 V 50 Hz 0 Pa"]