{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":38,"n_cols":6,"rows_kept":38,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXM-A8"]
[]
[]
[]
[]
["","","","","","RXM50A5V1B8"]
["Dimensiones","Unidad","","Altura","mm","610"]
["","","","Anchura","mm","923"]
["","","","Profundidad","mm","367"]
["Peso","Unidad","","","kg","40"]
["Motor del ventilador","Velocidad","Refrigeración","Súper baja","rpm","600"]
["Compresor","Tipo","","","","Compresor swing herméticamente sellado"]
["Límites de funcionamiento","Refrigeración","Ambiente","Mín.","°CBS","-10"]
["","","","Máx.","°CBS","50, 46"]
["","Calefacción","Ambiente","Mín.","°CBH","-21 (1), -15 (1)"]
["","","","Máx.","°CBH","18"]
["Nivel de presión sonora","Refrigeración","","Nom.","dBA","48"]
["","Calefacción","","Nom.","dBA","49"]
["Refrigerante","Tipo","","","","R-32"]
["","Carga","","","kg","0.95"]
["","Carga","","","tCO2Eq","0.65"]
["","GWP","","","","675"]
["Conexiones de tubería","Longitud de tubería","Máx.","Ud. ext. – Ud. int.","m","30"]
["","Carga de refrigerante adicional.","","","kg/m","002"]
["","Diferencia de nivel","Ud. int. – Ud. ext.","Máx.","m","20"]
["Accesorios estándar","Installation manual","","","","1"]
["","Drain joint","","","","1"]
["","Refrigerant charge label","","","","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1"]
["","General safety precautions","","","","1"]
["","LOT10 Energy Label","","","","1"]
["","Drain cap","","","","3"]
["Alimentación eléctrica","Fase","","","","1~"]
["","Frecuencia","","","Hz","50"]
["","Tensión","","","V","220-240"]
["Notas","","","","","(1) - Consulte la ilustración por separado para el rango de funcionamiento"]
["","","","","","(2) - Consulte en el plano independiente con los datos eléctricos."]
["","","","","","(3) - Contiene gases fluorados de efecto invernadero"]