{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":40,"n_cols":6,"rows_kept":40,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-F8"]
[]
[]
[]
[]
["","","","","","RXS71FAV1B8"]
["Ventilador","Caudal de aire","Refrigeración","Súper baja","m³/min","46.0"]
["","","Calefacción","Súper baja","m³/min","46.0"]
["","","","Súper baja","cfm","1624"]
["","","Calefacción","Súper baja","cfm","1624"]
["Dimensiones","Unidad","","Altura","mm","770"]
["","","","Anchura","mm","900"]
["","","","Profundidad","mm","320"]
["Peso","Unidad","","","kg","71"]
["Motor del ventilador","Velocidad","Refrigeración","Súper baja","rpm","730"]
["","","Calefacción","Súper baja","rpm","730"]
["Compresor","Tipo","","","","Compresor swing herméticamente sellado"]
["Límites de funcionamiento","Refrigeración","Ambiente","Mín.","°CBS","-10"]
["","","","Máx.","°CBS","46"]
["","Calefacción","Ambiente","Mín.","°CBH","-15"]
["","","","Máx.","°CBH","18"]
["Nivel de presión sonora","Refrigeración","","Alto","dBA","52"]
["","Calefacción","","Alto","dBA","52"]
["Refrigerante","Tipo","","","","R-410A"]
["","Carga","","","kg","2.3"]
["","Carga","","","tCO2Eq","4.8"]
["","GWP","","","","2087.5"]
["Conexiones de tubería","Longitud de tubería","Máx.","Ud. ext. – Ud. int.","m","30"]
["","Carga de refrigerante adicional.","","","kg/m","0,02 (para longitud de tubería superior a 10 m)"]
["","Diferencia de nivel","Ud. int. – Ud. ext.","Máx.","m","20"]
["Accesorios estándar","Installation manual","","","","1"]
["","Refrigerant charge label","","","","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1"]
["","Drain socket assy","","","","1"]
["Alimentación eléctrica","Fase","","","","1~"]
["","Frecuencia","","","Hz","50"]
["","Tensión","","","V","220-240"]
["Notas","","","","","(1) - 220 V"]
["","","","","","(2) - 230V"]
["","","","","","(3) - 240V"]